## 20231106
function | rules | explanation
ALL | on System#Boot then
DHW | #allowDHW = 1; | allow DHW function (0/1)
OTT | #allowOTThermostat = 1; | allow OTT Thermostat function (0/1)
PS | #allowPumpSpeed = 1; | allow PumpSpeed function (0/1)
SM | #allowSilentMode = 1; | allow SilentMode function (0/1)
SS | #allowSoftStart = 1; | allow SoftStart function (0/1)
SyncOT | #allowSyncOT = 1; | allow Sync OT function (0/1)
WAR | #allowWAR = 1; | allow WAR function (0/1)
ALL
SyncOT | #chEnable = -1; | #chEnable is clean ?chEnable
SyncOT OTT | #chEnableOffTime=-1; | Time?chEnable goes off
SyncOT | #chEnableTimeOff=-1; | ?chEnable Off Timer
OTT | #chSetPoint = -1; | copy of ?chEnable
OTT | #compRunTime = -1; | Time the compressor is running
OTT | #compStartTime = -1; | Time the compressor starts running
OTT | #compState = -1; | compressor state (0/1)
DHW | #DHWRun = -1; | DHWrun state (0/1)
DHW | #legionellaRunDay = 7; | 1 (Monday) .. 7 (Saturday)
OTT | #mainTargetTemp = -1; | Water Temperature target for HEAT
PS | #maxPumpDuty = 85; | value which fits my installation (~ 11l/m)
WAR SyncOT | #maxTa = -1;
SM | #mildMode = -1;
DHW | #prevHeatPumpState = -1;
DHW | #prevOperatingMode = -1;
SM | #quietMode = -1;
OTT SS | #softStartCorrection = 0;
SS | #softStartPhase = -1;
SyncOT OTT SM SS | #timeRef = -1;
ALL | setTimer(1,10); | main timer which calls all functions
SyncOT OTT | setTimer(2,15); | timer for time reference
ALL | end
ALL
ALL | on timer=1 then | main timer which calls all functions
WAR | calculateWAR(); | not required to remove them if you
SM | checkSilentMode(); | don't need them, this is done with
SyncOT | syncOpenTherm(); | the allow variable in the on boot
PS | maxPumpDuty(); | block
DHW | checkDHW();
OTT | OTThermostat();
ALL | setTimer(1,15); | run this function every 15 seconds
ALL | end
SyncOT OTT SS
SyncOT OTT SS | on timer=2 then | timer for time reference
SyncOT OTT SS | #timeRef = %day * 1440 + %hour * 60 + %minute; | sync #timeRef with current time
SyncOT OTT SS | setTimer(2,60); | run this function every minute
SyncOT OTT SS | end
SM
SM | on checkSilentMode then | SilentMode function
SM | if isset(@Outside_Temp) == 1 && isset(@Heatpump_State) then | Sets #silentmode value depending on
SM | if #allowSilentMode == 1 then | outside temperature and time of day
SM | #allowSilentMode = 0;
SM | if @Outside_Temp < 10 then
SM | #silentMode = 2;
SM | else
SM | #silentMode = 3;
SM | end
SM | if @Outside_Temp < 5 then
SM | #silentMode = 1;
SM | end
SM | if @Outside_Temp < 2 then
SM | if %hour > 22 ¦¦ %hour < 7 then
SM | #silentMode = 1;
SM | else
SM | #silentMode = 0;
SM | end
SM | end
SM | setTimer(3, 900); | this function runs every 15 minutes
SM | setQuietMode();
SM | end
SM | end
SM | end
SM
SM | on timer=3 then | reset allow parameter
SM | #allowSilentMode = 1;
SM | end
SM
SM | on setQuietMode then | Set QuietMode variable
SM | if #mildMode != -1 then | QuietMode will be #mildMode if
SM | #quietMode = #mildMode; | #mildMode is set, otherwise
SM | else | #silentMode
SM | #quietMode = #silentMode;
SM | end
SM | if @Quiet_Mode_Level != #quietMode then
SM | @SetQuietMode = #quietMode;
SM | end
SM | end
SyncOT
SyncOT | on syncOpenTherm then | Sync OT variable
SyncOT | if #allowSyncOT == 1 then
SyncOT | ?outletTemp = @Main_Outlet_Temp;
SyncOT | ?inletTemp = @Main_Inlet_Temp;
SyncOT | ?outsideTemp = @Outside_Temp;
SyncOT | ?dhwTemp = @DHW_Temp;
SyncOT | ?dhwSetpoint = @DHW_Target_Temp;
SyncOT | if ?chEnable == 1 then | chEnable update is with some logic to
SyncOT | #chEnable = 1; | keep #chEnable 1 if ?chEnable is 0 for
SyncOT | if #chEnableTimeOff != -1 then | only a short (5 minute) time
SyncOT | #chEnableTimeOff = -1;
SyncOT | #chEnableOffTime = -1;
SyncOT | end
SyncOT | else
SyncOT | if #chEnableTimeOff == -1 then
SyncOT | #chEnableTimeOff = #timeRef;
SyncOT | end
SyncOT | #chEnableOffTime = #timeRef - #chEnableTimeOff; | #chEnableOffTime gives time in
SyncOT | if #chEnableOffTime < 0 then | minutes ?chEnable = 0
SyncOT | #chEnableOffTime = #timeRef - #chEnableTimeOff + 10080;
SyncOT | end
SyncOT | if #chEnableOffTime > 5 then | #chEnable goes to 0 after 5 minutes
SyncOT | #chEnable = 0;
SyncOT | end
SyncOT | end
SyncOT | #dhwEnable = ?dhwEnable;
SyncOT | if #maxTa != -1 then | sync ?maxTa with result of the WAR
SyncOT | ?maxTSet = #maxTa; | function
SyncOT | end
SyncOT | if @Compressor_Freq == 0 then
SyncOT | ?flameState = 0;
SyncOT | ?chState = 0;
SyncOT | ?dhwState = 0;
SyncOT | else
SyncOT | ?flameState = 1;
SyncOT | if @ThreeWay_Valve_State == 0 then
SyncOT | ?chState = 1;
SyncOT | ?dhwState = 0;
SyncOT | else
SyncOT | ?chState = 0;
SyncOT | ?dhwState = 1;
SyncOT | end
SyncOT | end
SyncOT | end
SyncOT | end
WAR
WAR | on calculateWAR then | Calculate WAR setpoint function
WAR | if #allowWAR == 1 then
WAR | if isset(@Z1_Heat_Curve_Target_Low_Temp) == 1 && isset(@Z1_Heat_Curve_Outside_High_Temp) == 1 && isset(@Z1_Heat_Curve_Target_High_Temp) == 1 && isset(@Z1_Heat_Curve_Outside_Low_Temp) == 1 then
WAR | $Ta1 = @Z1_Heat_Curve_Target_Low_Temp;
WAR | $Tb1 = @Z1_Heat_Curve_Outside_High_Temp;
WAR | $Ta2 = 36;
WAR | $Tb2 = @Z1_Heat_Curve_Outside_Low_Temp;
WAR | if @Outside_Temp >= $Tb1 then
WAR | #maxTa = $Ta1;
WAR | else
WAR | if @Outside_Temp <= $Tb2 then
WAR | #maxTa = $Ta2;
WAR | else
WAR | #maxTa = 1 + floor(0.9 + $Ta1 + (($Tb1 - @Outside_Temp) * ($Ta2 - $Ta1) / ($Tb1 - $Tb2)));
WAR | end
WAR | end
WAR | end
WAR | #allowWAR = 0;
WAR | setTimer(5,900); | this function runs every 15 minutes
WAR | end
WAR | end
WAR
WAR | on timer=5 then
WAR | #allowWAR = 1;
WAR | end
PS
PS | on maxPumpDuty then | MaxPumpDuty function
PS | if #allowPumpSpeed == 1 then | Sets (water)pump speed depending on
PS | #allowPumpSpeed = 0;
PS | if @ThreeWay_Valve_State == 1 && @Max_Pump_Duty != 220 then | OM and compressor running or not
PS | @SetMaxPumpDuty = 220; | if production is HEAT or COOL the
PS | end | pumpspeed will depend on
PS | if @ThreeWay_Valve_State == 0 && @Heatpump_State == 1 then | @Outside_Temp as well
PS | if @Outside_Temp < 10 then
PS | $MPF = 11;
PS | else
PS | $MPF = 10;
PS | end
PS | if @Outside_Temp < 5 then
PS | $MPF = 12;
PS | end
PS | if @Outside_Temp < 2 then
PS | $MPF = 13;
PS | end
PS | if @Compressor_Freq == 0 then
PS | $MPF = 8;
PS | end
PS | if @Pump_Flow < $MPF then
PS | #maxPumpDuty = #maxPumpDuty + 5;
PS | else
PS | if @Pump_Flow > $MPF + 1 then
PS | #maxPumpDuty = #maxPumpDuty - 1;
PS | end
PS | end
PS | if #maxPumpDuty > 140 then
PS | #maxPumpDuty = 140;
PS | end
PS | if @Max_Pump_Duty != #maxPumpDuty then
PS | @SetMaxPumpDuty = #maxPumpDuty;
PS | end
PS | end
PS | setTimer(6, 60); | this function runs every minute
PS | end
PS | end
PS
PS | on timer=6 then
PS | #allowPumpSpeed = 1;
PS | end
DHW
DHW | on checkDHW then | DHW function
DHW | if #allowDHW == 1 then | DHW production will start if:
DHW | #allowDHW = 0; | - DHW_Temp < 39;
DHW | if @ThreeWay_Valve_State == 0 && (@DHW_Temp < 39 ¦¦ (%hour == 13 && (%day == #LegionellaRunDay ¦¦ @DHW_Temp < @DHW_Target_Temp + @DHW_Heat_Delta))) then | - DHW_Temp < DHW_Target +
DHW | #prevOperatingMode = @Operating_Mode_State; | DHW_Delta and %hour = 13;
DHW | #prevHeatPumpState = @Heatpump_State; | On Legionelladay a Legionella run
DHW | @SetOperationMode = 3; | will be done if %hour = 13.
DHW | if @Heatpump_State != 1 then
DHW | @SetHeatpump = 1;
DHW | end
DHW | if %day == #legionellaRunDay then
DHW | @SetForceSterilization = 1;
DHW | end
DHW | #DHWRun = 1;
DHW | end
DHW | if #DHWRun == 1 then
DHW | if @ThreeWay_Valve_State == 0 && @DHW_Temp > 49 then
DHW | @SetOperationMode = #OperatingModeLast;
DHW | if @Heatpump_State != #HeatPumpStateLast then
DHW | @SetHeatpump = #HeatPumpStateLast;
DHW | end
DHW | #OperatingModeLast = 3;
DHW | #HeatPumpStateLast = 1;
DHW | #DHWRun = -1;
DHW | end
DHW | end
DHW | setTimer(7,900); | this function runs every 15 minutes minute
DHW | end
DHW | end
DHW
DHW | on timer=7 then
DHW | #allowDHW = 1;
DHW | end
OTT
OTT | on OTThermostat then | Opentherm Thermostat function
OTT | if #allowOTThermostat == 1 && #DHWRun != 1 then | Switch HP on/off based on ?chEnable
OTT | if #chenable == 1 && @ThreeWay_Valve_State == 0 then | & Sync HP_Target with ?chSetpoint
OTT | if ?chSetpoint > 9 then | Prevent update setpoint if due to some
OTT | #chSetpoint = ?chSetpoint; | glitches ?chSetpoint = 0 which happens
OTT | end | sometimes.
OTT | softStart(); | Run softStart function (if allowed)
OTT | #mainTargetTemp = #chSetpoint + #softStartCorrection; | set #mainTargetTemp based on
OTT | if #mainTargetTemp < 20 then | #chSetpoint and #softStartCorrection
OTT | #mainTargetTemp = 20; | (if any). Safegards to prevent Target
OTT | end | below 20 and above 40 degrees.
OTT | if #mainTargetTemp > 40 then
OTT | #mainTargetTemp = 40;
OTT | end
OTT | #mainTargetTemp = floor(#mainTargetTemp);
OTT | if #compState == 1 then
OTT | if #mainTargetTemp + 2 < @Main_Outlet_Temp then | safegard to prevent Target way below
OTT | #mainTargetTemp = round(@Main_Outlet_Temp - 1.5); | @Main_outlet_Temp to prevent
OTT | end | compressor switch off.
OTT | end
OTT | if @Z1_Heat_Request_Temp != #mainTargetTemp then
OTT | @SetZ1HeatRequestTemperature = #mainTargetTemp;
OTT | end
OTT | if @Operating_Mode_State != 0 then | Set OM to HEAT
OTT | @SetOperationMode = 0;
OTT | end
OTT | if @Heatpump_State != 1 && #chEnable == 1 then | Set HP on if #chEnable = 1
OTT | @SetHeatpump = 1;
OTT | end
OTT | end
OTT | if #chEnableOffTime > 15 && @ThreeWay_Valve_State == 0 && (#compRunTime > 30 ¦¦ #compState == 0) && @Outside_Temp > 2 then | Set HP off if #chEnable is off for
OTT | @SetHeatpump = 0; | 15 minutes & compressor is off or
OTT | end | on for more than 30 minutes
OTT | #allowOTThermostat = 0;
OTT | setTimer(8,25); | this function runs every 30 seconds
OTT | end | (trigger from timer 1 every 15 sec.)
OTT | end
OTT
OTT | on timer=8 then
OTT | #allowOTThermostat = 1;
OTT | end
SS
SS | on softStart then | softStart function
SS | if #allowSoftStart == 1 && #compState == 1 then | This function tries to reduce the
SS | if #softStartPhase < 1 then | compressor frequency asap by setting
SS | #softStartPhase = 1; | QuietMode and reducing target temp
SS | setTimer(9,5); | to temp below current water temp.
SS | end | After this startup behavour it increases
SS | if #softStartPhase == 2 then | the target temp to prevent switch off
SS | #softStartCorrection = @Main_Outlet_Temp - 1 - #chSetpoint; | compressor for a set time (2 hours)
SS | end | After this phase it will gradualy reduce
SS | if #softStartPhase == 3 then | the correction value which will most
SS | if #chSetpoint <= @Main_Outlet_Temp then | likely lead to compressor off.
SS | #softStartCorrection = @Main_Outlet_Temp - 0.7 - #chSetpoint;
SS | end
SS | if #chSetpoint > @Main_Outlet_Temp then
SS | #softStartCorrection = @Main_Outlet_Temp + 1 - #chSetpoint;
SS | end
SS | end
SS | if #softStartCorrection > 5 && #chSetpoint != 10 then
SS | #softStartCorrection = 5;
SS | end
SS | if #softStartCorrection < -5 then
SS | #softStartCorrection = -5;
SS | end
SS | if @Compressor_Freq > 18 && @Compressor_Freq < 26 then | Set @QuietMode back to 0 when
SS | #mildMode = 0; | compressor < xx Hz
SS | setQuietMode();
SS | end
SS | end
SS | end
SS
SS | on timer=9 then
SS | if #softStartPhase == 4 then
SS | if #softStartCorrection > 0 then
SS | #softStartCorrection = #softStartCorrection - 1;
SS | setTimer(9,900); | phase 3 step correction timer
SS | else
SS | #softStartCorrection = 0;
SS | #softStartPhase = -1;
SS | end
SS | end
SS | if #softStartPhase == 3 then
SS | #softStartPhase = 4;
SS | setTimer(9,10);
SS | end
SS | if #softStartPhase == 2 then
SS | #softStartPhase = 3;
SS | setTimer(9,7200); | phase 2 timer
SS | end
SS | if #softStartPhase == 1 then
SS | #softStartPhase = 2;
SS | setTimer(9,120); | phase 1 timer
SS | end
SS | end
OTT SS
OTT SS | on @Compressor_Freq then
OTT SS | if @Compressor_Freq == 0 then
OTT SS | #compState = 0;
OTT SS | #softStartCorrection = 0;
OTT SS | #softStartPhase = -1;
OTT SS | if #mildMode != #silentMode then | Set @quietMode back to #silentmode value
OTT SS | #mildMode = #silentMode; | once compressor stops
OTT SS | setQuietMode();
OTT SS | end
OTT SS | else
OTT SS | if #compState < 1 then
OTT SS | #compStartTime = #timeRef;
OTT SS | #compState = 1;
OTT SS | end
OTT SS | #compRunTime = #timeRef - #compStartTime; | caclutate CompressorRunTime
OTT SS | if #compRunTime < 0 then
OTT SS | #compRunTime = #timeRef - #compStartTime + 10080;
OTT SS | end
OTT SS | end
OTT SS | end